Appendix No. 1 Quantitative and qualitative indicators of resources

for the technical specifications for the turnkey construction of the EPC project “Silleno Water Treatment and Wastewater Treatment Plant”

  - Provide water treatment equipment and systems with the following basic requirements:

  - Service and firefighting water production unit

| User | Norm. Consumption |  | Max. Consumption |  |
| --- | --- | --- | --- | --- |
|  | м3/h | м3/day | м3/h | м3/day |
| LTD «Silleno» (fire water) * | - | - | 1812,00 | 43487,20 |
| LTD «Silleno» (service water) ** | 1 | 12 | 19 | 150 |

* - filling firefighting tanks with firefighting water within 24 hours is not included in the water consumption balance; the pipeline capacity should be determined based on the requirements for refilling firefighting tanks within 24 hours;

** - The calculation of service water is based on a periodic consumption of 1 m3/h at power stations for 3 hours 4 times a day. The maximum consumption of service water is determined by the water consumption of 150 m3 for backwashing refrigerators to remove salt deposits on the walls of the refrigerator tubes for 8 hours once a day. The frequency is determined as necessary;

Note:

1) The capacity of the service and firefighting water supply system shall be determined by the project; the capacity of the pumping station shall be determined by the project.

2) For the service and firefighting system, provide all necessary connections for technical flows, assuming their continuous operation.

    - Pressure and temperature requirements at the border of Silleno LLP:

| Operating parameters |  |  |  |  |  | Design parameters |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Temperature (°C) |  |  | Pressure (МPа) |  |  | Temperature (°C) | Pressure (МPа) |
| min | norm | max | min | norm | max |  |  |
| 5 | 20 | 30 | 0,4 | 0,5 | 0,6 | 30 | 1,0 |

    - Quality composition of service and firefighting water at Silleno LLP:

| Parameters | Value | Recommended values for design |
| --- | --- | --- |
| pH |  | 7,5-8,5 |
| COD | mg/L | 15-16,7 |
| TSS | mg/L | 5-9 |
| TOC | mg/L | 3,4-3,8 |
| TDS | mg/L | 400-500 |
| Hardness | ppm | 199-221 |
| Alkalinity | ppm | 210-233 |
| Cations |  |  |
| Ammonium | mg/L | 0,6 |
| Potassium | mg/L | 2,0 |
| Sodium | mg/L | 46,8 |
| Magnesium | mg/L | 20,2 |
| Calcium | mg/L | 55,2 |
| Strontium | mg/L | 0 |
| Barium | mg/L | 0 |
| Iron | mg/L | 0,1 |
| Manganese | mg/L | 0 |
| Copper | mg/L | 0 |
| Aluminum | mg/L | 0,1 |
| Аnions |  |  |
| Carbonate | mg/L | 0,9 |
| Bicarbonate | mg/L | 282,0 |
| Nitrates | mg/L | 0,4 |
| Fluorides | mg/L | 0,1 |
| Chlorides | mg/L | 47,7 |
| Sulfates | mg/L | 25,0 |
| Polyphosphates | mg/L | 0,2 |
| Silicon dioxide | mg/L | 2,5 |
| Boron | mg/L | 0 |

  - Note:

*- parameters must be specified by the developer during the design process.

** - water for firefighting and service needs must be treated with a biocide.

Unit of demineralized water production

| Consumers | Norm. Consumption |  | Max Consumption |  |
| --- | --- | --- | --- | --- |
|  | м3/h | м3/day | м3/h | м3/day |
| Silleno LLP | 111,50* | 2676,00 | 131,5** | 3156,0 |

* Normal consumption is calculated based on the constant supply of demineralized water to the steam production circuit at the pyrolysis plant to meet the boiler room's needs for the production of heating water for the Complex. Constant consumption. Must be taken into account in the Silleno consumption balance.

    - Requirements for the pressure and temperature of demineralized water at the boundary of Silleno LLP:

| Operating parameters |  |  |  |  |  | Design parameters |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Temperature (°C) |  |  | Pressure (МPа) |  |  | Temperature (°C) | Pressure (МPа) |
| min | norm | max | min | norm | max |  |  |
| 10 | 30 | 30 | 0,6 | 0,75 | 0,8 | -38 / 75 | 1,0 |

    - Requirements for the quality composition of demineralized water from Silleno LLP:

| Parameters | Value | Recommended values for design |
| --- | --- | --- |
| pH | pH | 8,0-9,0 |
| Electrical conductivity | µS/cм | <0,1 |
| TDS | mg/L | <0,1 |
| Oil content | mg/L | Not detectable |
| Total hardness (CaCO3) | mg/L | <0,1 |
| Cations |  |  |
| Calcium | mg/L | <0,001 |
| Barium | mg/L | <0,001 |
| Magnesium | mg/L | Not detectable |
| Sodium | mg/L | <0,001 |
| Potassium | mg/L | Not detectable |
| Iron | mg/L | Not detectable |
| Copper | mg/L | Not detectable |
| Ammonia | mg/L | Not detectable |
| Аnions |  |  |
| Chlorides | mg/L | <0,001 |
| Silicon oxide | mg/L | <0,001 |
| Sulfates | mg/L | Not detectable |
| Nitrates | mg/L | <0,001 |
| Bicarbonates | mg/L | Not detectable |
| Carbonates | mg/L | Not detectable |

  - Unit of a clarified water production facility to feed cooling towers in a recirculating water supply system

| Consumers | Norm. Consumption |  | Max Consumption |  |
| --- | --- | --- | --- | --- |
|  | м3/h | м3/day | м3/h | м3/day |
| Silleno LLP | 1990 | 47760 | 2085,00 | 50039,50 |

    - Requirements for the pressure and temperature of clarified water (clarified) in the network at the border of Silleno LLP:

| Parameters of desalinated water in the network at the border of Silleno LLP | Operating parameters |  |  | Design parameters |
| --- | --- | --- | --- | --- |
|  | Min | Norm | Max | Min Max |
| Pressure, МPа | 0,60 | 0,75 | 0,8 | 1,4 |
| Temperature (°C) | 15 | 20 | 25 | 30 |

    - Quality composition of clarified water for Silleno LLP:

| Parameters |  | Value |  | Recommended values for design |
| --- | --- | --- | --- | --- |
| pH |  | pH |  | 6-8 |
| COD |  | mg/L |  | <10,3 |
| TSS |  | mg/L |  | <4,6 |
| TOC |  | mg/L |  | <2,4 |
| TDS* |  | mg/L |  | 310-390 |
| Hardness |  | ppm |  | 122,8-136,4 |
| Alkalinity |  | ppm |  | 137,6-152,9 |
| Cations |  |  |  |  |
| Ammonium | mg/L |  | 0,4 |  |
| Potassium | mg/L |  | 1,3 |  |
| Sodium | mg/L |  | 34,8 |  |
| Magnesium | mg/L |  | 12,4 |  |
| Calcium | mg/L |  | 34,2 |  |
| Strontium | mg/L |  | 0 |  |
| Barium | mg/L |  | 0 |  |
| Iron | mg/L |  | 0 |  |
| Manganese | mg/L |  | 0 |  |
| Copper | mg/L |  | 0 |  |
| Aluminum | mg/L |  | 0,1 |  |
| Anions |  |  |  |  |
| Carbonate | mg/L |  | 0,6 |  |
| Bicarbonate | mg/L |  | 185,4 |  |
| Nitrates | mg/L |  | 0,2 |  |
| Fluorides | mg/L |  | 0,1 |  |
| Chlorides | mg/L |  | 32 |  |
| Sulfates | mg/L |  | 15,5 |  |
| Polyphosphates | mg/L |  | 0,2 |  |
| Silicon dioxide | mg/L |  | 1,5 |  |
| Boron | mg/L |  | 0 |  |

Note:

* - The TDS parameter may be changed to 483.6 mg/L for a period of 24 hours while firefighting tanks are being refilled.

  - Sanitary and drinking water production facilities

| Users | Norm Consumption |  | Мax Consumption |  |
| --- | --- | --- | --- | --- |
|  | м3/h | м3/day | м3/h | м3/day |
| Silleno LLP* | 25,00 | 432,00 | 27,00 | 648,00 |

* - Twice a day to replenish drinking water tanks. Duration up to 6 hours. Taking into account the simultaneous operation of 3 emergency showers, as well as consumption to maintain the specified humidity in production and administrative buildings.

Note:

1.    Drinking water quality shall comply with GOST 2874-82.

2.    The source of the initial water supply is the Astrakhan-Mangyshlak main water pipeline, with the quality and quantity indicators of the water presented below.

1.4. Requirements for pressure and temperature of sanitary and drinking water in the network at the border of Silleno LLP:

| Parameters in the network at the border of Silleno LLP | Value | min | norm | max | Design parametres* |
| --- | --- | --- | --- | --- | --- |
| Pressure | МPа | 0.4 | 0.5 | 0.6 |  |
| Temperature | °С | 5 | 30 | 40 |  |

*parameters must be specified by the developer during the design process

- Provide for treatment plant equipment and systems with the following basic requirements:

  - Treatment of industrial storm water (K4 system) with a capacity of:

| Sources | Norm. Consumption |  | Max Consumption |  |
| --- | --- | --- | --- | --- |
|  | м3/h | м3/day | м3/h | м3/day |
| Silleno LLP Contaminated rainwater runoff K4 | 20,00 | 480,00 | 150,00 | 3600,00* |
| Silleno LLP Conditionally clean wastewater K2 | - | - | 5000,00** | 10000,00 |

* - potentially possible amount of runoff, taking into account a fire of 10,800 m3 over 72 hours. This flow should not be taken into account in the water supply balance, but treatment facilities must be ready to accept this runoff and treat it if necessary. During a fire, pumping is not carried out;

** - conditionally clean runoff from undeveloped areas + conditionally clean runoff from technological areas after the first washout (30 minutes of rain). Runoff is pumped out within 2 hours once every 5 days;

    - Indicators of the composition of industrial storm water (system K4) discharged from the facilities of the second stage of Silleno LLP (industrial storm water – during rain):

| Parameters |  | Value | Recommended values for design |  |
| --- | --- | --- | --- | --- |
| рН |  | рН | 5 ÷ 10 |  |
| COD |  | mg/L | 40 - 2 500 |  |
| BOD |  | mg/L | 9 - 1 200 |  |
| Oil content |  | mg/L | 50 – 2 000 (Max. 10 000) |  |
| TSS |  | mg/L | 200 - 900 (max. 2000) |  |
| TDS |  | mg/L | 20-1500 (max. 3000) |  |
| Organic substances |  |  |  |  |
| Benzene | mg/L |  |  | < 30 |
| Phenol | mg/L |  |  | < 30 |
| Methanol | mg/L |  |  | < 50 |
| Ethylbenzene | mg/L |  |  | < 5 |
| Toluene | mg/L |  |  | < 5 |
| Na2S | mg/L |  |  | <20 |

    - Indicators of the composition of industrial and storm wastewater (system K4) discharged from the facilities of the second stage of Silleno LLP (industrial and storm wastewater – for dry weather):

| Parameters | Value | Recommended values for design |
| --- | --- | --- |
| Temperature | °C | 5 - 40 |
| pH | - | 5 - 10 |
| TSS | mg/L | 50 - 500 |
| COD | mgO2/L | 40 - 600 |
| BOD5 | mgO2/L | 9 - 300 |
| Free Oil/HC | mg/L | 0,04 - 25 |
| TDS | mg/L | 100 - 500 |
| Organic substances |  |  |
| Phenol | mg/L | 1 - 50 |
| Methanol | mg/L | 100 |
| Benzene | mg/L | 10 – 25 Max 50 |
| Toluene | mg/L | 5 |
| Ethylbenzene | mg/L | 5 |

    - Indicators for the composition of conditionally clean storm water (system K2) discharged from the facilities of the second stage of Silleno LLP:

| Parameters | Value | Recommended values for design |
| --- | --- | --- |
| Temperature | °C |  |
| pH | - | 6 - 9 |
| TSS | mg/L | 700 max |
| COD | mgO2/L | 100 max |
| BOD5 | mgO2/L | 20 max |
| TOC | mg/L | NN |
| Free Oil/HC | mg/L | 10 max |
| TDS | mg/L | 200 max |
| Organic substances |  |  |
| Sulfates | mg/L | 30 max |
| Chlorides | mg/L | 50 max |

Take into account the following parameters at the border of Silleno LLP:

| Parameters * | Norm | Design parameters |
| --- | --- | --- |
| Temperature (°C) | 5-40 | -38 до 75 |
| Pressure, МPа | 0,4/0,5/0,6 | 1.2 |

* - на источнике

  - Treatment of chemically contaminated (salt-containing) wastewater (K14 system), as well as flushing of cooling towers and boilers.

| Sources | Norm. Consumption |  | Max Consumption |  |
| --- | --- | --- | --- | --- |
|  | м3/h | м3/day | м3/h | м3/day |
| Silleno LLP Salt-containing effluents – low salt content (TDS) K14.1 | 590,00 | 14160,00 | 700,00* | 16 450,00 |
| Silleno LLP High-salinity effluents (HTDS) K14.2 | 12,00 | 288,00 | 15 | 333 |

* - backwash drains of the cooling tower side filter once every 5-7 days for 21 hours a day;

    - Indicators of the composition of chemically contaminated wastewater discharged from the facilities of Silleno LLP (salt-containing effluents with low salt content (TDS) K14.1).

| Parameters |  | Value | Recommended values for design |
| --- | --- | --- | --- |
| Temperature | °C |  | <45 |
| pH | - |  | 7,5-8,7 |
| TSS* | mg/L |  | <1500 |
| COD | mgO2/L |  | < 300 |
| BOD5 | mgO2/L |  | < 300-350 |
| Free Oil/HC | mg/L |  | <5 |
| TDS | mg/L |  | 760-1800 |
| Hardness | mg/L CaCO3 |  | 200 - 460 |
| Alkalinity | mg/L CaCО3 |  | <350 |
| Cations |  |  |  |
| Ammonium | mg/L |  | 2,4-62,6 |
| Sodium | mg/L |  | 20,0-192 |
| Calcium | mg/L |  | 26,4-88,32 |
| Magnesium | mg/L |  | 4,0-44,4 |
| Iron | mg/L |  | 0,2-0,28 |
| Manganese | mg/L |  | 0,5-0,6 |
| Aluminum | mg/L |  | 0,5-1,2 |
| Copper | mg/L |  | 0,24-0,6 |
| Zinc | mg/L |  | < 4 |
| Potassium | mg/L |  | < 5,12 |
| Аnions |  |  |  |
| Chlorides | mg/L |  | 40-145 |
| Sulfates | mg/L |  | 20-60,8 |
| Bicarbonates | mg/L |  | 80-614,4 |
| Nitrates | mg/L |  | 0,5-0,93 |
| Nitrites | mg/L |  | 0,25-0,6 |
| Phosphates | mg/L |  | 0,2-15 |
| Silicon dioxide | mg/L |  | 10-14,3 |
| Fluorides | mg/L |  | <0,4 |
| Amines | mg/L |  | <50 |

    - Pressure and temperature requirements for salt-containing wastewater – with low salt content in the network at the border of Silleno LLP:

| Operating parameters |  |  |  |  |  | Design parameters |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Temperature (°C)** |  |  | Pressure (МPа) |  |  | Temperature (°C) | Pressure (МPа) |
| min | norm | max | min | norm | max |  |  |
| 5 | 25 | 40 | 0,4 | 0,5 | 0,6 | -27,3 / 75 | 1,0 |

Indicators of the composition of chemically contaminated wastewater discharged from the facilities of the second stage of Silleno LLP (high-salinity wastewater (HTDS) K14.2):

| Parameters | Value | Recommended values for design |
| --- | --- | --- |
| Temperature | °C | 5 - 40 |
| pH | - | 6 - 8 |
| TSS | mg/L | 350 |
| COD | mg O2/L | 2800 |
| BOD5 | mg O2/L | 1400 |
| TOC | mg/L | NN |
| Free Oil/HC | mg/L | 8 – 20 norm 300 max |
| TDS | mg/L | 130 000 |
| Cations |  |  |
| Ammonium | mg/L | 130 – 408,8 |
| Potassium | mg/L | NN |
| Sodium | mg/L | 180 – 8 413,6 norm 10 000 max |
| Calcium | mg/L | 10 – 323 norm 425 max |
| Magnesium | mg/L | 76 - 100 |
| Anions |  |  |
| Chlorides | mg/L | 25 – 1 530 norm 2 000 max |
| Sulfates | mg/L | 100 – 17 111 norm 20 000 max |
| Sulfides | mg/L | ≤1 |
| Bicarbonates | mg/L | 100 - 6500 |
| Sulfites | mg/L | 300 - 30000 |
| Nitrates | mg/L | 1-28 |
| Nitrites | mg/L | 13- 24 |
| Silicon dioxide | mg/L | 100 norm 142 max |
| Organic substance |  |  |
| Phenol | mg/L | 50 |
| Methanol | mg/L | 30 |
| Amines | mg/L | 50 |
| Ethylbenzene | mg/L | 5 |
| Toluene | mg/L | 5 |
| Benzene | mg/L | 10 – 25 max. 50 |

| Parameters at the borders | Value | min | norm | max | Design parameters |
| --- | --- | --- | --- | --- | --- |
| Pressure | mPа | 0.4 | 0.5 | 0.6 | 1.0 |
| Temperature (°C) | °С | 5 | 30 | 40 | -27,3 до 75 |

  - Treatment of domestic wastewater, with a capacity of:

| Sources | Norm. Consumption |  | Max Consumption |  |
| --- | --- | --- | --- | --- |
|  | м3/h | м3/day | м3/h | м3/day |
| «Silleno» LTD | 10,00 | 100,00 | 27,00 | 215,00*** |

Note:

* - to be clarified by the developer during design;

*** - the maximum flow rate is determined based on the simultaneous consumption of domestic and drinking water at the Complex in different areas, taking into account the flow from the dining room.

    - Indicators of the composition of domestic wastewater at Silleno LLP

| Parameters | Unit of measurement |  |  | Value |
| --- | --- | --- | --- | --- |
| pH | pH |  |  | 6-9 |
| COD | mg/L |  |  | <300 |
| BOD | mg/L |  |  | <150 |
| Oil-containing | mg/L |  |  | <5 |
| Suspended solids TSS, max | mg/L |  |  | ˂40 |
| Dissolved solids (TDS) | mg/L |  |  | 300-1300 |
| NH3-N, max | mg/L |  |  | ˂15 |
| NO3-N, max | mg/L |  |  | ˂20 |
| NO2-N, max | mg/L |  |  | ˂0.6 |
| NO2 | mg/L |  |  | ˂0.6 |
| Са2+ | mg/L |  |  | 120 |
| Mg2+ | mg/L |  |  | 50 |
| SO4 2- | mg/L |  |  | 320 |
| SiO2 | mg/L |  |  | 20 |
| НСО3 | mg/L |  |  | 500 |
| Сl- | mg/L |  |  | 200 |
| Parameters of domestic wastewater in the network at the border of Sileno LLP | Operating parameters |  |  | Design parameters |
|  | Min | Norm | Max |  |
| Pressure*, МPа | 0,4 | 0,5 | 0,6 | 1,0 |
| Temperature (°C) | 5 | 25 | 40 | -38 / 75 |

Note:

* Pressure parameters must be specified by the developer during design, taking into account the pressure difference in Sileno projects.

  - Source water parameters

  - Qualitative and quantitative indicators of source water (Astrakhan-Mangyshlak water pipeline)

| Parameters | Unit of measurement | Value |
| --- | --- | --- |
| Odor at 20 °C | points | 1 |
| Taste | points | 0 |
| Color | degree of color | 31,6 |
| Turbidity | mg/dm³ | 46,5 |
| Dry residue | mg/dm³ | 366 |
| Level, pH | pH | 10,8 |
| Free chlorine | mg/dm³ | <0,71 |
| Combined chlorine | mg/dm³ | - |
| Ammonia | mg/dm³ | 0,7 |
| Nitrites | mg/dm³ | 0,025 |
| Nitrates | mg/dm³ | 0,358 |
| Chlorides | mg/dm³ | 47,7 |
| Sulfates | mg/dm³ | <20,0 |
| Iron Fe | mg/dm³ | 0,434 |
| Polyphosphates | mg/dm³ | 0,5 |
| Copper Cu | mg/dm³ | 0,0019 |
| Aluminum Al | mg/dm³ | 0,355 |
| Petroleum products | mg/dm³ | 0,028 |
| Surfactants (SAS) | mg/l | 0,31 |
| Alkalinity | mg/dm³ | 3,1 |
| Calcium Ca | mg/l | 69 |
| Mg | mg/l | 25,2 |
| Bicarbonates | mg/l | 189,1 |
| Suspended particles | mg/l | 189,1 |
| BOD | mg O2/l | 1,52 |
| COD | mg O2/l | 23,9 |
| TDS | mg/dm³ | 366 |
| Hardness | mol/l | 4,8 |
| Strontium Sr | mg/l | <0,001 |
| Sodium Na | mg/l | 18 |
| Potassium K | mg/l | <4,0 |
| Barium Ba | mg/l | 0,036 |
| Silicon dioxide | mg/l | 4,967 |
| Fluorides | mg/l | 0,25 |
| Boron | mg/l | 0,037 |
| Manganese | mg/l | 0,019 |
| Carbonates | mg/l | <8,0 |
| Carbonate alkalinity | mg/l | <0,4 |
| Phosphates | mg/l | 0,4 |
| Phosphorus | mg/l | 0,75 |
| Hydrogen sulfide | mg/l | <0,002 |